How to set up OPC with Simatic Net
By Jesper M. Pedersen. December 2004.

The below example assumes that you want to setup OPC communications with Simatic Net and a CP5611 card. If you have other hardware, you have to adapt the example to suit.

Preconditions:

A PC with Windows 2000 with SP3 or better, or Windows XP with SP1.

(note: At the time this document was written, 

SIMATIC NET was NOT compatible with Windows XP with SP2).

One available PCI slot for the Siemens CP5611 card.

Simatic Net software ”Profibus Softnet S7”.

CP5611 Profibus/MPI PCI card.

Step 1:
Install SIMATIC NET software from the installation CD. 

If STEP7 IS installed: Be sure to deselect SIMATIC NCM PC/S7
If STEP7 is NOT installed: Be sure to select SIMATIC NCM PC/S7

[image: image1.jpg]SIMATIC NCM PL/S7 V5.2
Sotwae for conuing SHATICNET PC products;
Pot necessan i

ot higher s instalied

Beadme.

e\program flestsiemens\simationem Biowse.

Requiedonc: 326MByte  Avaiableonc: 14572 MByte





 
Notice: The installation will require approx 30 minutes and 2 reboots to complete.

Step 2:
Install the CP5611 card in a PCI slot in the PC.


When the PC restarts, it will start the SIMATIC NCM PC Wizard. 

 
Close it, do NOT use it for setting up the S7 connection (!).

Step 3:
Select Start\SIMATIC NCM PC Manager. 


choose Options..Set PG/PC interface.

[image: image2.jpg]hecessPath |
‘Access Point of the Application:
[S7onine
(Standard for STEP 7)

> PC rtemal (acal]

Iteiface Parameter Assignment Lsec:

P riemal focal — | Pt
WEPESH[PRDF\Busl <htive>
> SMCEZ Card 1

| Eop0
_';1 Dekle
>

{Communication vith SIMATIC companerts
in this PG/PC]





Set the Interface Parameter Assignment Used to PC internal (local).

Note: This is required in order to be able to ”download” the configuration of the OPC server.

If STEP7 is installed, later (when setup of SIMATIC NET is finished) the S7ONLINE access point can be changed to CP5611 or CP5511 for example for online access to S7 PLCs.

Step 4:
Choose File..New

[image: image3.jpg]24 SIMATIC NCM PC Manager

AltiF

or anew lbrar





Choose any meaningful name (”CIM WDP” is used throughout becuase it was required by the authors original application).

[image: image4.jpg]s s | Mok |

Name [ Starage path
locpiiC:AProgram Fles\SIEMENS\SIMATIC.NCMProfects\acpi

I Addito cunert multiproject
Name: Type:
e [Pt

Storage location [path}

[T Program Fles\SIEMENS\GIMATIC NCMAG7prcl. Browse.






Choose Insert..Station..Simatic PC Station.

[image: image5.png]3 SIMATIC NCM PC Manager - [CIM WDP.
EP Fle Edt Insert PLC View Options Window | Help

D[22 4 [5]e] i

TR r—) |

Press F1 to get Help.

[ESVATTE PE Statont 1]

R e ey





Change the name of SIMATIC PC Station(1) to the computer name.

Use Start..Settings..Control Panel..System..Computer Name tab to find the computer name

Notice: There will be a period ”.” in the name reported by the Windows Control Panel.

Do NOT include the period in the name for the station.

Example: Name reported by Control Panel: ”DISA_CIM_01.” 

Then set the station name to ”DISA_CIM_01”.

Also, the name is case sensitive. Set it exactly as indicated in Control Panel, except the period.

[image: image6.png]System Restore
General Computer Name Hardware Advanced

| Ml

Computer descrition:

21|

| Automatic Updates Renote

the follawing information o dentiy your computer

DISA CIMPC T

For examy
Computer

Kitchen Computer” or "Maiy's

Full computer name:

DISA_CM_01.

Wolkgroup:

To use the Network deni
domain and create alocal
ID.

To tename tis computer o on a domain cick Change.

WORKGROUP

fication Wizard to fon a
user account,click Network

Change.

ply

Cance




 [image: image7.png]SIMATIC PC Station

General | Setings | Configuation

Name: DISA_CIM_01

S’m}vwage location [C:\Program Files\SIEMENS\SIMATIC.NCM\S 7proi\Cim_wd_1 ﬂ

Author:

Conment =





 
Double-click on configuration to start SIMATIC NET PC Config:

[image: image8.png][ SIMATIC NCM PC Manager - [CIM WDP -- C:\Program Files)\SIEMENS\SIMATICNEMIS 0ro) o [ |
EPFle Edt Insert PLC View Options Window Help

lsixl
Dile{Es] [ i Sl ir—- ]

ChwoP
£ DISA_CM_01

Press F1 to get Help. [PCinternal (local) 7





Step 5:
Insert an OPC server in index 1 and a CP 5611 in index 4.

To insert a module: Highligt the ”slot” in the left side of the window, and double-click on the 

module in the right side of the window.

[image: image9.png]) Station Edit Insert PLC View Options Window Help

: =lolx|
=l81x]

=

2 (8% g =le sl [@e| 28 el

OPC Server

5

H

B

Rl (0N

Incl Mode

Comm

1 OPC Server

CPEeIT

I cr it
I crsirza
§ cpsirzazn
o) Pt
s

=3 CPelt

{§ swve0sPs
oreessr———
(0 cPas13A2
{2 cPE8I3FD
0 cPss1
0 cPas14A2
0 cPE8I4FD
User Application
Applcation
= OPC Server
SWVBO'5PS
S/ VE.0 5P
5w VB
SWVE2SPT

Press F1 ta get Help.

EY

[GGK 561-1AADD 3]
SIMATIC NET CP 5611 PROFIBUS, 57
connections, DP master, DPYT, DP Slave,

PG functions, DP mster lass 2, PCl b

fchg /|





When inserting the CP5611 card, accept the default settings (--- not networked ---) when the first dialog is presented. Click OK.


[image: image10.png]Properties - PROFIBUS interface CP 5611 (R0/54)

General  Parameters |

Address: 2| Ifasubret s seected.
the next available address is suggested.

Subret

Hew.

Fiopees |
e |

Cancel Help





Note: Never mind that it says PROFIBUS interface if you want to use MPI.

Double click on the CP 5611 to open the Object Properties dialog.

[image: image11.png]P 5611

General

Shart Desciption:

Assigment

Orcr No./ fimware.

Nae:

Intetface
Tope:
Address:

Networked:

Comment:

Gl
2

No

Operating Mode | Reserve LG4RS

cPset

6GKT 56114400 /VE.05
CPset

SIMATIC NET CP 5511 PROFIBUS, 57 cornections, OP maste, DFYA, = |
OP slve, PG unctions, DP master dass 2, PC| bus g, SINATIC
NET 0 772001 5P

iH

1|

X0

=

Help





 
Set Interface type to MPI and click on Properties…
 
(Note: Some applications require Interface type to be Profibus rather than MPI.

 
In that case, be sure to set Profile to Standard rather than DP)

[image: image12.png]General  Parameters |

e

Highest address: 31

Transrission rate: 167.5 Kbps

Subret
[

reaked

New

Fispeiles

Delete

o Cwcel |t





Set Address to the MPI node that you want the PC to have in the network (here10) and select the MPI(1) network.

Click on Properties to open the interface settings.

[image: image13.png]General| Network Setings |

Highest MPY address: 31 =] T Change.

Transmission ate:

132Kbps
137 5 iy

Mibps
5 Mbps
12Mbos

Coned e





Set Transmission rate to want you want the entire MPI network has, not just the PC (here 1.5 Mbps).
(Note: If there is an S7-300 in the MPI network, then Transmission Rate will be limited to 187.5 Kbps. (exception at this time of writing: S7-317 PN/DP).

Clik OK in all dialog boxes to close them.


Choose Options..Configure Network to start NetPro.

[image: image14.png]Instal 65D file.

= CPPROFIBUS -

cPaatt
CP5a1242
CPaa12A2H

O cpsn
o
=0 cpsen
SwveosRe
SWVBOSPS...
@ P

. CPEEI13 AD





Step 6: 
In NetPro highligt OPC Server and choose Insert..New Connection.

[image: image15.png]=10l
B Network Edit | Insert PLC View Options Window Help. =18 x|
B[R (g G tewows oS bl g x|
MPI(1) =
VP! B s e
DISA_CIM_01
T
||| ;l_'
[Loca & artner & [Parner [rywe |
< i >
Inserts & new connection in the connection table.





 
Click OK to select the default Connection partner = (Unspecified) 

 
with a Type = S7 connection.
[image: image16.png]- Connecton Partner

'@ In the curent project
= &) O woP
(Urspecie]
i boadeast sttons
Bl makicst taons
Bp Inurkrown prect

PO

Stators [{Unspeciied)

Modile
P
Type: 57 comection <]

W% Disply propeies befoe nseiing

) Cancel Help





 
The Properties dialog will open automatically:

[image: image17.png]General | 0pC | Status Irfomation

-Local Connection End Point
= Eived corfinured dyiic cormeciion

- Connestion identfication

LocallD
W | e [wor
IV Establish an active connection VFD Name:
I~ Send opersing mote messages [OFC Server
|- Connection Path
Local Pattzer
T Unspeciied
Inteface: P 5611 Unspeciied
Subnet MPIT) P E]
Adess i 5

Address Delais

=

Help





Set Local ID to what you want it to be known as when browsing OPC (here WDP) and match the Partner Address with the MPI address of the remote S7 CPU (here is set to 5). 

(Notice: Some applications require a different Partner Address. 

An MPI or Profibus address of 2 is very common for the remote CPU)

 
Click on Address Details…

[image: image18.png]Local Partner
Connection Resource:
G — o





 
The Partner Rack/Slot values must match the remote S7 CPU hardware position.

 
For an S7-300 the slot value is typically 2.

 
For an S7-400 the slot value is typically 2 or 3.

Step 7:
In NetPro, choose Network..Save and Compile. 

[image: image19.png]% NetPro - [CIM WDP (Network) — C:\Program File:
B8 \otwork Edt Insert PLC View Options Window

b ST

(% %) 8| Dle| dnfia| 5] 5|

Bl »el

MPI(1)
MPI

DISA_CIM_01

0

Bl s s |

e R ——

ull

LocalD Pariner D

Partner

[rype =

a

Ready

e

X237 v 198 |[insert [Chg





 
Close Simatic NCM PC Manager

Step 8:
Select Start\Station Configurator (or click on the icon in the taskbar).

[image: image20.png][« R 2





(
[image: image21.png]Components | Disgnostcs |

Station: {msA,ﬂM_m

Mode:

JRUN_P

miex

Firg

Status

Fun/Stop | Comn

add.

=

|

Dol

| Ao

Stalion Name.._ |

ImportStation .

|

Disable Stalion |

FEs





 
Click on  Add.. 

 
Then add a Component of type OPC server at Index 1.

[image: image22.png][Add Component

Type:

It

Name: Application

Parameter asic =l

= 0 F





(
[image: image23.png](EEafion Configuration Edtor - FONLINE)  MRRRAGSER 21

Components | Disgnostcs |

Statiors  [DISA_CIM_01 Mode: [RUN_P.

ndex | Name Tpe Fing ] Status | Fu/Stop | Dom ] =
1 [ pplcation OPC Server E ©

i =

New disgnostc enty arivecl

add. Edt | o | Ao ]

Stalion Name.. Import Staton .| Disable Stalion |

i





 
Close Station Configuration Editor.

Step 9:
Select Start..Simatic..SIMATIC NET..Settings..Configuration Console.

[image: image24.png]=lolx|

Ble acton Vew tep
- | B8m @
|23 pC station

General _Miodule properties

588 SIMATIC KT Configuration
8 opicstons Type of modle: FROFIELS
) 2 Mad:‘:ssm Made of the modue: Configured mode. B
5 General Index |+ ]
g Version Name of the module:
adress
Intrface prfle for Sl
& Network Diagnos: ki
5" Bus fadks IR
CPS611(PROFIBUS) <Active>

B softne 0P trace | P20 HEROE
BB Intel®) PROJ1000 C | |CpBgtiFwL)

@ smiion
o Module reaction:

A Access points
bt
o | e

[The mod was entered in Staion Canfigiation
Editor and registered or the configured mode.





 
Set the CP5611 mode to Configured mode and specify Index = 4.

 
Activate with Apply.

[image: image25.png]=lolx|

Help

Bl Action ew

- | B8m @

Select OPC protocol

RC statin
5 B SIMATIC T Confguration
Aoplcstions

=08 OPC settings

Symbols
@ orCuace
@ Frotocolrace

Wodes

2 Accessponts

The P Server can support various protocols a the same time.
Here, you selectthe protocols it wil supprt.

I~ oP T~ FMS
v s7 I SR
T~ DP master class 2

T~ SNMP

eqardless of the setings made here.
‘Additonall the configured data exchange DX can be activated.

v DX

The PROFIditve DPC Server and the highperfomance i process DF-OPC Serv

T~ FDL
T~ PROF
T~ PROF

Aply Cancel Help





 
Set the selected OPC protocols to S7 only (all others deselected).

 
Activate with Apply.

 
Close Configuration Console.

Step 10: Select Start\Station Configurator.

[image: image26.png](EEafion Configuration Edtor - FONLINE)  MRRRAGSER 21

Components | Disgnostcs |

Statiors  [DISA_CIM_01

Mode:

JRUN_P

Index | Name

Tope Fing

Status | Aun/Stop | Com

1 [ pplcation

T cpsent

OPC Server

cPsett

E ©
E o

|

New disgnostc enty arivecl

add.

=

Depie. | Amon |

Staion e

ImportStation .. |

Disable Stalion |





 
The CP 5611 should now appear in index 4.

Step 11:Switch to NetPro. 

 
Highligt all the PC components as shown (1) 

 
Select Network..Save and compile (2)


and select PLC..Download to current project..Selected stations (3).

[image: image27.png]‘etPro - [CIM WDP (Network) - \ 1Bl
5 tetork_ b et PLC sew Optons sidon b =lafx|

=(8[m)] o slelwll 8 o2 ezt vl

MPI(1) 3 ~
MPI

ol

To display the connection table, please select a module capable
of a connection (CPU, FM module, OPC server or application).

Rk o e et





(
[image: image28.png]Stop Target Modules

The folowing modues wilbe stopped forloading o the system
data

Modile nce
OPC Server 1
CPse1t 4

o o





 
You will be prompted to accept the various components to be stopped. Accept with OK.

 
Close NetPro.

Step 12:Select Start\Station Configurator.

[image: image29.png](EEafion Configuration Edtor - FONLINE)  MRRRAGSER 21

Components | Disgnostcs |

Statiors  [DISA_CIM_01

Mode:

JRUN_P

Index | Name

Tope Fing

Status | Aun/Stop | Com

10 orCsena

T cpsent

OPC Server

cPsett

BE o B

E o

|

New disgnostc enty arivecl

add.

=

Depie. | Amon |

Staion e

ImportStation .. |

Disable Stalion |





 
Both OPC Server and CP5611 should now have no errors (no red cross at status icon).

 
If so, the configuration of SIMATIC NET is finished.


Close Station Configuration Editor.

Step 13:Use an OPC test client to test the connection.

Simatic Nets OPC test client is called OPC scout.

Start it. A dialog will appear with a list of available OPC servers. 

OPC.SimaticNET must be in the list. Right-click on it and it will ”connect”.

Specify any name for ”group”.

Right-click on the newly created group - NOT on (New group), and select Add item.

A dialog will appear where you can click on available connections.

Pick items that you want to add, and add them to the list of updated items in the group with 

the ”-->” button.

You should now be able to see the values of the items update online.

(no screenshots available at this time – sorry).

Finally:
Typical pitfalls.

1. Is the PG/PC interface set to internal ?

2. Is the name of the computer specified correctly everywhere ?

The Station Name in NCM must be the same as in Station Configurator as well as the name of the PC as indicated in the Control Panel.

No period in the end of the name.

Case must be the same (NAME, Name and name are all different)

3. The mode of the communication hardware must be configured with the proper index in Configuration Console.

4. The correct slot number is not specified for the communication partner when setting up the connection in NetPro.







_1164543836.doc
[image: image1.png]Properties - PROFIBUS interface CP 5611 (R0/54)

General  Parameters |

Address: 2| Ifasubret s seected.
the next available address is suggested.

Subret

Hew.

Fiopees |
e |

Cancel Help








